## Document tracking (hidden)
Effluent Quality Data for Publishing
| Name | Date | Signature
Created by: | Victoria Corling
Revised by:
Aproved By:
TRIM File Number
Location: | Googong WRP Offspec tank
EPA License No | 20188

## June 2017
Googong WRP Monthly Effluent quality monitoring
Results for the month of: June 2017
Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  |  |  |  | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
BOD | 10 | 0 | 0 | 0 | Yes | [5 empty] | 2017-06-06 | 7.3 | 420 | <2 | 0.015 | 0.066 | 4.9 | 0.009 | <2 | <1
Chlorine(free) | 0.1 | 0.015 | 0.015 | 0.015 | Yes | [5 empty] | 2017-06-13 | 7.42 | 398 | 2 | 0.015 | 0.036 | 4.37 | 0.022 | <2 | <1
Faecal Coliforms | 150 | 0 | 0 | 0 | Yes | [5 empty] | 2017-06-20 | 7.16 | 411 | 3 | 0.015 | 0.08 | 4.16 | 0.018 | <2 | <1
Ammonia | 2 | 0.0515 | 0.08 | 0.024 | Yes | [5 empty] | 2017-06-27 | 7.5 | 381 | <2 | 0.015 | 0.024 | 4.81 | 0.065 | <2 | <1
Total Nitrogen | 10 | 4.56 | 4.9 | 4.16 | Yes | [5 empty] | average | 7.345 | 402.5 | 2.5 | 0.015 | 0.0515 | 4.56 | 0.0285 | 0 | 0
PH | 6.5-8.5 | 7.345 | 7.5 | 7.16 | Yes | [5 empty] | max | 7.5 | 420 | 3 | 0.015 | 0.08 | 4.9 | 0.065 | 0 | 0
Phophorus | 0.5 | 0.0285 | 0.065 | 0.009 | Yes | [5 empty] | min | 7.16 | 381 | 2 | 0.015 | 0.024 | 4.16 | 0.009 | 0 | 0
TSS | 10 | 2.5 | 3 | 2 | Yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of June 2017
|  |  | SITE 1 | SITE 4 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9 | SITE 10
|  | Sample Date | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15
|  | Matrix | Water | Water | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 41 | 42 | 46 | 46 | 46 | 160 | 160 | 120
TN | mg/L | 0.05 | 0.5 | 0.42 | 0.41 | 0.38 | 0.44 | 1.3 | 0.42 | 1.1
TP | mg/L | 0.01 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 0.02 | <0.02 | <0.02
BOD | mg/L | 5 | bar: SITE 1 to SITE 10
TSS | mg/L | 5 | <5 | <5 | <5 | <5 | <5 | 12 | <5 | <5
TDS | mg/L | 10 | 75 | 73 | 86 | 87 | 85 | 360 | 450 | 390
Free Chlorine | mg/L | 0.1 | 0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | 5 | 4 | 5 | 4 | 5 | 3 | <2 | 4
pH | No unit | 0 | 7.1 | 7.2 | 7.3 | 7.4 | 7.4 | 8 | 7.7 | 7.8
Ammonia | mg/L | 0.01 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02
Escgherichia coli | cfu/ 100ml | 1 | 44 | 4 | 6 | 5 | 12 | 9 | 32 | 2
Thermotolerant Coliforms | cfu/ 100ml | 1 | 44 | 4 | 6 | 5 | 12 | 9 | 32 | 2
Intestical Enterococci | cfu/ 100ml | 1 | 9 | 4 | 1 | 6 | 4 | 2 | 21 | 2
Total Algae | cells/ml | ND | 2614 | 3222 | 2041 | 1488 | 2735 | 398 | 366 | 670

## May 2017
Googong WRP Monthly Effluent quality monitoring
Results for the month of: May 2017
Pollutants | 90th percentile limits mg/l | average of 5 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  |  |  |  | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
BOD | 10 | 4 | 4 | 4 | Yes | [5 empty] | 2017-05-02 | 7.71 | 434 | 3 | <0.03 | 0.542 | 3.56 | 0.013 | <2 | <1
Chlorine(free) | 0.1 | 0 | 0 | 0 | Yes | [5 empty] | 2017-05-09 | 7.02 | 501 | <2 | <0.03 | 0.306 | 3.13 | 0.015 | 4 | <1
Faecal Coliforms | 150 | 0 | 0 | 0 | Yes | [5 empty] | 2017-05-16 | 7.52 | 459 | 2 | <0.03 | 0.024 | 4.38 | 0.011 | <2 | <1
Ammonia | 2 | 0.1902 | 0.542 | 0.024 | Yes | [5 empty] | 2017-05-23 | 7.64 | 427 | <2 | <0.03 | 0.051 | 3.86 | 0.009 | <2 | <1
Total Nitrogen | 10 | 3.718 | 4.38 | 3.13 | Yes | [5 empty] | 2017-05-30 | 7.66 | 429 | <2 | <0.03 | 0.028 | 3.66 | 0.018 | <2 | <1
PH | 6.5-8.5 | 7.51 | 7.71 | 7.02 | Yes | [5 empty] | average | 7.51 | 450 | 2.5 | 0 | 0.1902 | 3.718 | 0.0132 | 4 | 0
Phophorus | 0.5 | 0.0132 | 0.018 | 0.009 | Yes | [5 empty] | max | 7.71 | 501 | 3 | 0 | 0.542 | 4.38 | 0.018 | 4 | 0
TSS | 10 | 2.5 | 3 | 2 | Yes | [5 empty] | min | 7.02 | 427 | 2 | 0 | 0.024 | 3.13 | 0.009 | 4 | 0
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of May 2017
|  |  | SITE 1 | SITE 4 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9 | SITE 10
|  | Sample Date | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15 | 2017-05-15
|  | Matrix | Water | Water | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 43 | 43 | 47 | 44 | 44 | 130 | 200 | 160
TN | mg/L | 0.05 | 0.31 | 0.39 | 0.3 | 0.34 | 0.4 | 2.2 | 0.26 | 0.86
TP | mg/L | 0.01 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 0.25 | <0.02 | <0.02
BOD | mg/L | 5 | bar: SITE 1 to SITE 10
TSS | mg/L | 5 | bar: SITE 1 to SITE 10
TDS | mg/L | 10 | 73 | 67 | 83 | 74 | 69 | 360 | 470 | 440
Free Chlorine | mg/L | 0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | 3 | <2 | <2 | <2 | <2 | 3 | <2 | 3
pH | No unit | 0 | 7.8 | 7.9 | 7.9 | 8 | 8 | 7.9 | 8.2 | 8.2
Ammonia | mg/L | 0.01 | 0.04 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03 | <0.01 | 0.04
Escgherichia coli | cfu/ 100ml | 1 | 8 | 7 | 12 | 17 | 10 | 80 | 98 | 55
Thermotolerant Coliforms | cfu/ 100ml | 1 | 8 | 7 | 12 | 17 | 10 | 80 | 98 | 55
Intestical Enterococci | cfu/ 100ml | 1 | 2 | 8 | 16 | 7 | 11 | 600 | 31 | 54
Total Algae | cells/ml | ND | 3112 | 5877 | 5915 | 4343 | 4073 | 247 | 531 | 148

## April 2017
Googong WRP Monthly Effluent quality monitoring
Results for the month of: April 2017
Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  |  |  | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
BOD | 10 | 0 | <2 | <2 | Yes |  |  |  |  | 2017-04-04 | 7.72 | 463 | 1 | <0.03 | 0.015 | 2.39 | 0.012 | <2 | <1
Chlorine(free) | 0.1 | 0 | <0.03 | <0.03 | Yes |  |  |  |  | 2017-04-11 | 7.54 | 444 | 7 | <0.03 | 0.069 | 2.76 | 0.012 | <2 | <1
Faecal Coliforms | 150 | 1 | 1 | 1 | Yes |  |  |  |  | 2017-04-18 | 7.58 | 415 | 2 | <0.03 | 0.356 | 2.76 | 0.011 | <2 | <1
Ammonia | 2 | 0.17275 | 0.356 | 0.015 | Yes |  |  |  |  | 2017-04-26 | 7.62 | 437 | 3 | <0.03 | 0.251 | 3.16 | 0.02 | <2 | 1
Total Nitrogen | 10 | 2.7675 | 3.16 | 2.39 | Yes |  |  |  |  | average | 7.615 | 439.75 | 3.25 | #DIV/0! | 0.17275 | 2.7675 | 0.01375 | #DIV/0! | 1
PH | 6.5-8.5 | 7.615 | 7.72 | 7.54 | Yes |  |  |  |  | max | 7.72 | 463 | 7 | 0 | 0.356 | 3.16 | 0.02 | 0 | 1
Phophorus | 0.5 | 0.01375 | 0.02 | 0.011 | Yes |  |  |  |  | min | 7.54 | 415 | 1 | 0 | 0.015 | 2.39 | 0.011 | 0 | 1
TSS | 10 | 3.25 | 7 | 1 | Yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of April 2017
|  |  | SITE 1 | SITE 4 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9
|  | Sample Date | 2017-04-10 | 2017-04-10 | 2017-04-10 | 2017-04-10 | 2017-04-10 | 2017-04-10 | 2017-04-10
|  | Matrix | Water | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 40 | 42 | 50 | 44 | 45 | 110 | 140
TN | mg/L | 0.05 | 0.59 | 0.62 | 0.54 | 0.6 | 0.52 | 1.2 | 0.89
TP | mg/L | 0.01 | <0.02 | <0.02 | <0.02 | <0.02 | 0.09 | 0.09 | 0.04
BOD | mg/L | 5 | bar: SITE 1 to SITE 9
TSS | mg/L | 5 | <5 | 6 | 16 | <5 | 6 | 120 | 13
TDS | mg/L | 10 | 62 | 77 | 95 | 83 | 76 | 210 | 300
Free Chlorine | mg/L | 0.1 | 0.1 | <0.1 | <0.1 | 0.1 | 0.1 | 0.1 | 0.1
Oil and Grease | mg/L | 5 | 2 | 3 | <2 | <2 | <2 | <2 | <2
pH | No unit | 0 | 7.7 | 7.6 | 7.8 | 8 | 7.8 | 7.6 | 8.3
Ammonia | mg/L | 0.01 | 0.02 | 0.06 | 0.01 | <0.01 | 0.01 | 0.02 | 0.02
Escgherichia coli | cfu/ 100ml | 1 | 400 | 600 | 100 | 62 | 120 | 1300 | 1400
Thermotolerant Coliforms | cfu/ 100ml | 1 | 400 | 600 | 100 | 62 | 120 | 1300 | 1400
Intestical Enterococci | cfu/ 100ml | 1 | 56 | 370 | 330 | 130 | 140 | 21000 | 5200
Total Algae | cells/ml | ND | 2783 | 1546 | 3548 | 3076 | 3298 | 1075 | 1323

## March 2017
Googong WRP Monthly Effluent quality monitoring
Results for the month of: March 2017
Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  |  |  | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
BOD | 10 | 2 | 2 | 2 | Yes |  |  |  |  | 2017-03-07 | 7.39 | 449 | 1 | 0.015 | 0.014 | 2.79 | 0.023 | 2 | <1
Chlorine(free) | 0.1 | 0 | <0.03 | <0.03 | Yes |  |  |  |  | 2017-03-14 | 7.71 | 523 | 3 | 0.015 | 0.017 | 2.07 | 0.016 | <2 | <1
Faecal Coliforms | 150 | 0 | <1 | <1 | Yes |  |  |  |  | 2017-03-21 | 7.48 | 460 | 4 | 0.015 | 0.205 | 2.93 | 0.013 | <2 | <1
Ammonia | 2 | 0.06525 | 0.205 | 0.014 | Yes |  |  |  |  | 2017-03-28 | 7.57 | 447 | 1 | 0.015 | 0.025 | 2.21 | 0.015 | <2 | <1
Total Nitrogen | 10 | 2.5 | 2.93 | 2.07 | Yes |  |  |  |  | average | 7.5375 | 469.75 | 2.25 | 0.015 | 0.06525 | 2.5 | 0.01675 | 2 | #DIV/0!
PH | 6.5-8.5 | 7.5375 | 7.71 | 7.39 | Yes |  |  |  |  | max | 7.71 | 523 | 4 | 0.015 | 0.205 | 2.93 | 0.023 | 2 | 0
Phophorus | 0.5 | 0.01675 | 0.023 | 2.21 | Yes |  |  |  |  | min | 7.39 | 447 | 1 | 0.015 | 0.014 | 2.07 | 0.013 | 2 | 0
TSS | 10 | 2.25 | 4 | 1 | Yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of March 2017
|  |  | SITE 1 | SITE 4 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9 | SITE 10
|  | Sample Date | 2017-03-20 | 2017-03-20 | 2017-03-20 | 2017-03-20 | 2017-03-20 | 2017-03-20 | 2017-03-20 | 2017-03-20
|  | Matrix | Water | Water | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 41 | 42 | 46 | 43 | 44 | 76 | 140 | 210
TN | mg/L | 0.05 | 0.5 | 0.48 | 0.49 | 0.47 | 0.46 | 3.1 | 0.64 | 0.49
TP | mg/L | 0.01 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 0.06 | <0.02
BOD | mg/L | 5 | bar: SITE 1 to SITE 10
TSS | mg/L | 5 | bar: SITE 1 to SITE 10
TDS | mg/L | 10 | 89 | 63 | 96 | 71 | 88 | 470 | 530 | 560
Free Chlorine | mg/L | 0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | 3
pH | No unit | 0 | 7.5 | 7.5 | 7.7 | 7.7 | 7.6 | 7.4 | 7.5 | 8
Ammonia | mg/L | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.37 | 0.02 | 0.01
Escherichia coli | cfu/ 100ml | 1 | 60 | 64 | 70 | 99 | 58 | 160 | 1300 | 1000
Thermotolerant Coliforms | cfu/ 100ml | 1 | 60 | 64 | 70 | 99 | 58 | 160 | 1300 | 1000
Intestical Enterococci | cfu/ 100ml | 1 | 16 | 20 | 120 | 76 | 37 | 400 | 800 | 1000
Total Algae | cells/ml | ND | 4590 | 30601 | 13205 | 6949 | 9515 | 214 | 835 | 131

## February 2017
Googong WRP Monthly Effluent quality monitoring
Results for the month of: February 2017
Pollutants | 90th percentile limits mg/l | average of 5 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  |  |  | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
BOD | 10 | 0 | <2 | <2 | Yes |  |  |  |  | 2017-02-01 | 7.71 | 470 | 1 | <0.03 | 0.014 | 2.62 | 0.154 | <2 | <1
Chlorine(free) | 0.1 | 0 | <0.03 | <0.03 | Yes |  |  |  |  | 2017-02-07 | 7.59 | 453 | 3 | <0.03 | 0.315 | 3.24 | 0.055 | <2 | <1
Faecal Coliforms | 150 | 0 | <1 | <1 | Yes |  |  |  |  | 2017-02-14 | 7.52 | 452 | 2 | <0.03 | 0.337 | 3.09 | 0.031 | <2 | <1
Ammonia | 2 | 0.4762 | 1.69 | 0.014 | Yes |  |  |  |  | 2017-02-21 | 7.66 | 504 | 2 | <0.03 | 1.69 | 3.64 | 0.056 | <2 | <1
Total Nitrogen | 10 | 3.106 | 3.64 | 2.62 | Yes |  |  |  |  | 2017-02-28 | 7.37 | 488 | 1 | <0.03 | 0.025 | 2.94 | 0.033 | <2 | <1
PH | 6.5-8.5 | 7.57 | 7.71 | 7.37 | Yes |  |  |  |  | average | 7.57 | 473.4 | 1.8 | #DIV/0! | 0.4762 | 3.106 | 0.0658 | #DIV/0! | #DIV/0!
Phophorus | 0.5 | 0.0658 | 0.154 | 0.031 | Yes |  |  |  |  | max | 7.71 | 504 | 3 | 0 | 1.69 | 3.64 | 0.154 | 0 | 0
TSS | 10 | 1.8 | 3 | 1 | Yes |  |  |  |  | min | 7.37 | 452 | 1 | 0 | 0.014 | 2.62 | 0.031 | 0 | 0
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of Feburary 2017
|  |  | SITE 1 | SITE 4 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9
Sample Date
|  | Matrix | Water | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 45 |  | 47 | 43 | 43 | 140
TN | mg/L | 0.05 | 0.49 |  | 0.83 | 0.4 | 0.42 | 2
TP | mg/L | 0.01 | <0.01 |  | <0.01 | <0.01 | <0.01 | <0.01
BOD | mg/L | 5 | bar: SITE 1; SITE 5 to SITE 8
TSS | mg/L | 5 | <5 |  | <5 | <5 | 11 | 24
TDS | mg/L | 10 | 97 |  | 94 | 93 | 88 | 520
Free Chlorine | mg/L | 0.1 | <0.1 |  | <0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | bar: SITE 1; SITE 5 to SITE 8
pH | No unit | 0 | 7.9 |  | 7.9 | 8 | 7.9 | 7.9
Ammonia | mg/L | 0.01 | 0.02 |  | 0.01 | 0.01 | 0.01 | 0.03
Escherichia coli | cfu/ 100ml | 1 | 52 |  | 80 | 400 | 110 | 500
Thermotolerant Coliforms | cfu/ 100ml | 1 | 52 |  | 80 | 400 | 110 | 500
Intestical Enterococci | cfu/ 100ml | 1 | 18 |  | 57 | 58 | 33 | 81
Cyanophyta | cells/ml | ND | 10500 |  | 5200 | 3600 | 6000 | ND
Total Potentially toxic Species | cells/ml | ND | bar: SITE 1; SITE 5 to SITE 8
Aphanocapsa | cells/ml | ND | 10500 |  | 5200 | 3600 | 6000 | -
Chlorophyta | cells/ml | ND | 7000 |  | 6300 | 7600 | 6400 | 1300
Diatoms(Bacillaropihyta) | cells/ml | ND | 5100 |  | 1600 | 1900 | 2000 | 280

## January 2017
Googong WRP Monthly Effluent quality monitoring
Results for the month of: January 2017
Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  |  |  | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
BOD | 10 | 0 | <2 | <2 | Yes |  |  |  |  | 2017-01-03 | 7.69 | 443 | 1 | <0.03 | 0.019 | 2.81 | 0.084 | <2 | <1
Chlorine(free) | 0.1 | 0 | <0.03 | <0.03 | Yes |  |  |  |  | 2017-01-10 | 7.71 | 445 | 4 | <0.03 | 0.015 | 3.15 | 0.17 | <2 | <1
Faecal Coliforms | 150 | 0 | <1 | <1 | Yes |  |  |  |  | 2017-01-17 | 7.74 | 446 | 1 | <0.03 | 0.011 | 3.05 | 0.243 | <2 | <1
Ammonia | 2 | 0.016 | 0.019 | 0.011 | Yes |  |  |  |  | 2017-01-25 | 7.8 | 389 | 2 | <0.03 | 0.019 | 2.92 | 0.366 | <2 | <1
Total Nitrogen | 10 | 2.9825 | 3.15 | 2.81 | Yes |  |  |  |  | average | 7.735 | 430.75 | 2 | #DIV/0! | 0.016 | 2.9825 | 0.21575 | #DIV/0! | #DIV/0!
PH | 6.5-8.5 | 7.735 | 7.8 | 7.69 | Yes |  |  |  |  | max | 7.8 | 446 | 4 | 0 | 0.019 | 3.15 | 0.366 | 0 | 0
Phophorus | 0.5 | 0.21575 | 0.366 | 0.084 | Yes |  |  |  |  | min | 7.69 | 389 | 1 | 0 | 0.011 | 2.81 | 0.084 | 0 | 0
TSS | 10 | 2 | 4 | 1 | Yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of January 2017
|  |  | SITE 1 | SITE 4 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9
|  | Sample Date | 2017-01-18 | 2017-01-18 | 2017-01-18 | 2017-01-18 | 2017-01-18 | 2017-01-18 | 2017-01-18
|  | Matrix | Water | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 49 | 44 | 46 | 58 | 50 | 230 | 44
TN | mg/L | 0.05 | 0.83 | 0.52 | 0.41 | 0.41 | 0.46 | 1.2 | 0.41
TP | mg/L | 0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | 0.06 | <0.01
BOD | mg/L | 5 | bar: SITE 1 to SITE 9
TSS | mg/L | 5 | <5 | <5 | <5 | <5 | 11 | 9 | <5
TDS | mg/L | 10 | 87 | 88 | 93 | 100 | 92 | 580 | 95
Free Chlorine | mg/L | 0.1 | 0.2 | 0.1 | 0.2 | 0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | bar: SITE 1 to SITE 9
pH | No unit | 0 | 7.6 | 7.7 | 7.6 | 7.8 | 7.6 | 7.8 | 7.7
Ammonia | mg/L | 0.01 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.03 | <0.01
Escgherichia coli | cfu/ 100ml | 1 | 100 | 23 | 500 | 64 | 24 | 32 | 120
Thermotolerant Coliforms | cfu/ 100ml | 1 | 100 | 23 | 500 | 64 | 24 | 32 | 120
Intestical Enterococci | cfu/ 100ml | 1 | 160 | 48 | 460 | 110 | 100 | 280 | 180
Cyanophyta | cells/ml | ND | 600 | 600 | 3900 | 1000 | 1750 | 820 | 2400
Total Potentially toxic Species | cells/ml | ND | bar: SITE 1 to SITE 9
Aphanocapsa | cells/ml | ND | 400 | 600 | 3600 | 1000 | 900 | - | 1600
Chlorophyta | cells/ml | ND | 2720 | 5400 | 3560 | 6320 | 5200 | 720 | 2120
Diatoms(Bacillaropihyta) | cells/ml | ND | 50 | 680 | 920 | 340 | 840 | 260 | 260

## December 2016
Googong WRP Monthly Effluent quality monitoring | [9 empty] | pH | TDS mg/L | TSS mg/L | Free chlorine mg/L | Ammonia mg/L-N | Total Nitrogen mg/L-N | Total Phosphorous mg/L-P | BOD mg/L | Thermotolerant Feacal Coliforms (confirmed) CFU/100ml
Results for the month of: December 2016
Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply | No | Yes |  | 2016-12-06 | 7.8 | 574 | 3 | <0.03 | 0.036 | 3.21 | 0.021 | <2 | <1
BOD | 10 | 0 | <2 | <2 | Yes |  |  |  | 2016-12-13 | 7.62 | 473 | 2 | <0.03 | 0.027 | 3.7 | 0.033 | <2 | <1
Chlorine(free) | 0.1 | 0 | <0.03 | <0.03 | Yes |  |  |  | 2016-12-20 | 7.75 | 452 | 1 | <0.03 | 0.021 | 3.89 | 0.454 | <2 | <1
Faecal Coliforms | 150 | 0 | <1 | <1 | Yes |  |  |  | 2016-12-28 | 7.8 | 510 | 2 | <0.03 | 0.015 | 3.25 | 0.095 | <2 | <1
Ammonia | 2 | 0.02475 | 0.036 | 0.015 | Yes |  |  |  | average | 7.7425 | 502.25 | 2 | #DIV/0! | 0.02475 | 3.5125 | 0.15075 | #DIV/0! | #DIV/0!
Total Nitrogen | 10 | 3.5125 | 3.89 | 3.21 | Yes |  |  |  | max | 7.8 | 574 | 3 | 0 | 0.036 | 3.89 | 0.454 | 0 | 0
PH | 6.5-8.5 | 7.7425 | 7.8 | 7.62 | Yes |  |  |  | min | 7.62 | 452 | 1 | 0 | 0.015 | 3.21 | 0.021 | 0 | 0
Phophorus | 0.5 | 0.15075 | 0.454 | 0.021 | Yes
TSS | 10 | 2 | 3 | 1 | Yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of December 2016
|  |  | SITE 1 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9
|  | Sample Date | 2016-12-22 | 2016-12-22 | 2016-12-22 | 2016-12-22 | 2016-12-22 | 2016-12-22
|  | Matrix | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 41 | 53 | 44 | 46 | 100 | 86
TN | mg/L | 0.05 | 0.56 | 0.55 | 0.63 | 0.56 | 2.5 | 0.55
TP | mg/L | 0.01 | <0.01 | <0.01 | <0.01 | <0.01 | 0.27 | <0.01
BOD | mg/L | 5 | bar: SITE 1 to SITE 9
TSS | mg/L | 5 | <5 | <5 | <5 | <5 | <5 | 13
TDS | mg/L | 10 | 70 | 83 | 75 | 87 | 370 | 350
Free Chlorine | mg/L | 0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | bar: SITE 1 to SITE 9
pH | No unit | 0 | 8 | 7.9 | 7.8 | 7.8 | 7.8 | 7.9
Ammonia | mg/L | 0.01 | 0.08 | 0.13 | 0.04 | 0.05 | 0.05 | 0.03
Escgherichia coli | cfu/ 100ml | 1 | 3 | 32 | 58 | 13 | 17 | 400
Thermotolerant Coliforms | cfu/ 100ml | 1 | 6 | 32 | 58 | 19 | 17 | 400
Intestical Enterococci | cfu/ 100ml | 1 | 23 | 51 | 66 | 17 | 130 | 79

## November 2016
Googong WRP Monthly Effluent quality monitoring
Results for the month of: November 2016
| Pollutants | 90th percentile limits mg/l | average of 5 samples (mg/l) | max (mg/l) | min (mg/l) | Comply
| BOD | 10 | <2 | <2 | <2 | yes
| Chlorine(free) | 0.1 | <0.03 | <0.03 | <0.03 | yes
| Faecal Coliforms | 150 | <1 | <1 | <1 | yes
| Ammonia | 2 | 2 | 0.02 | 0.02 | yes
| Total Nitrogen | 10 | 3.17 | 3.48 | 2.97 | yes
| PH | 6.5-8.5 | 7.8 | 7.94 | 7.55 | yes
| Phophorus | 0.5 | 0.025 | 0.04 | 0.02 | yes
| TSS | 10 | 1.25 | 2 | 1 | yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of November 2016
|  |  | SITE 1 | SITE 5 | SITE 6 | SITE 7 | SITE 8 | SITE 9
|  | Sample Date | 2016-11-10 | 2016-11-10 | 2016-11-10 | 2016-11-10 | 2016-11-10 | 2016-11-10
|  | Matrix | Water | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 40 | 50 | 42 | 45 | 200 | 140
TN | mg/L | 0.05 | 0.38 | 0.37 | 0.4 | 0.32 | 0.98 | 0.83
TP | mg/L | 0.01 | <0.01 | 0.01 | 0.01 | 0.02 | 0.02 | <0.01
BOD | mg/L | 5 | bar: SITE 1 to SITE 9
TSS | mg/L | 5 | <5 | <5 | <5 | <5 | <5 | 15
TDS | mg/L | 10 | 86 | 83 | 71 | 77 | 400 | 280
Free Chlorine | mg/L | 0.1 | <0.1 | <0.1 | <0.1 | <0.1 | 0.1 | <0.1
Oil and Grease | mg/L | 5 | bar: SITE 1 to SITE 9
pH | No unit | 0 | 7.3 | 7.7 | 7.8 | 7.6 | 8.3 | 7.9
Escgherichia coli | cfu/ 100ml | 1 | 1 | <1.0 | 16 | 19 | 24 | 80
Thermotolerant Coliforms | cfu/ 100ml | 1 | 1 | <1.0 | 16 | 19 | 24 | 80
Intestical Enterococci | cfu/ 100ml | 1 | 3 | 2 | 2 | 8 | 7 | 56
Cyanophyta | cells/ml | ND | bar: SITE 1 to SITE 9
Chlorophyta | cells/ml | ND | 840 | 880 | 580 | 440 | 3350 | 2650
Diatoms(Bacillaropihyta) | cells/ml | ND | 3550 | 4150 | 3350 | 4400 | 820 | 4900

## October 2016
Googong WRP Monthly Effluent quality monitoring
Results for the month of: October 2016
| Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply
| BOD | 10 | <2 | <2 | <2 | yes
| Chlorine(free) | 0.1 | <0.03 | <0.03 | <0.03 | yes
| Faecal Coliforms | 150 | <1 | <1 | <1 | yes
| Ammonia | 2 | 0.19 | 0.32 | 0.04 | yes
| Total Nitrogen | 10 | 2.6 | 2.99 | 1.64 | yes
| PH | 6.5-8.5 | 7.69 | 7.55 | 7.49 | yes
| Phophorus | 0.5 | 0.053 | 0.013 | 0.047 | yes
| TSS | 10 | 1.25 | 2 | 1 | yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data
QPRC Googong SW Monitoring
Results for the Month of October 2016
|  |  | SITE 1 | SITE 6 | SITE 7 | SITE 8 | SITE 9
|  | Sample Date | 2016-10-13 | 2016-10-13 | 2016-10-13 | 2016-10-13 | 2016-10-13
|  | Matrix | Water | Water | Water | Water | Water
Analyte Name | Units | Reporting Limit | Result | Result | Result | Result | Result
Alkalinity | mg/L | 5 | 35 | 40 | 43 | 160 | 99
TN | mg/L | 0.05 | 0.52 | 0.69 | 0.45 | 1.2 | 0.75
TP | mg/L | 0.01 | <0.01 | 0.02 | 0.02 | 0.04 | <0.01
BOD | mg/L | 5 | <5 | <5 | <5 | <5 | <5
TSS | mg/L | 5 | <5 | 21 | <5 | 11 | <5
TDS | mg/L | 10 | 82 | 89 | 89 | 320 | 260
Free Chlorine | mg/L | 0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Oil and Grease | mg/L | 5 | <5 | <5 | <5 | <5 | <5
pH | No unit | 0 | 7.1 | 7.7 | 7.5 | 7.7 | 7.4
Ammonia | mg/L | 0.01 | 0.05 | 0.04 | 0.05 | 0.03 | <0.01

## September 2016
Googong WRP Monthly Effluent quality monitoring
Results for the month of: September 2016
Pollutants | 90th percentile limits mg/l | average of 4 samples (mg/l) | max (mg/l) | min (mg/l) | Comply
BOD | 10 | <2 | <2 | <2 | yes
Chlorine(free) | 0.1 | <0.03 | <0.03 | <0.03 | yes
Faecal Coliforms | 150 | <1 | <1 | <1 | yes
Ammonia | 2 | 0.08 | 0.18 | 0.03 | yes
Total Nitrogen | 10 | 2.5 | 2.99 | 1.64 | yes
PH | 6.5-8.5 | 7.46 | 7.55 | 7.4 | yes
Phophorus | 0.5 | 0.03 | 0.08 | 0.01 | yes
TSS | 10 | 1 | 1 | 1 | yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data

## August 2016
Googong WRP Monthly Effluent quality monitoring
Results for the month of: August 2016
Pollutants | 90th percentile limits mg/l | average of 5 samples (mg/l) | max (mg/l) | min (mg/l) | Comply
BOD | 10 | <2 | <2 | <2 | yes
Chlorine(free) | 0.1 | <0.03 | <0.03 | <0.03 | yes
Faecal Coliforms | 150 | <1 | <1 | <1 | yes
Ammonia | 2 | 0.07 | 0.1 | 0.02 | yes
Total Nitrogen | 10 | 3.29 | 3.63 | 2.74 | yes
PH | 6.5-8.5 | 7.32 | 7.46 | 7.07 | yes
Phophorus | 0.5 | 0.02 | 0.04 | 0.02 | yes
TSS | 10 | 1.2 | 2 | 1 | yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data

## July 2016
Googong WRP Monthly Effluent quality monitoring
Results for the month ending: July 26th
Pollutants | 90th percentile limits mg/l | sample (mg/l) | Comply
BOD | 10 | <2 | yes
Chlorine(free) | 0.1 | <0.03 | yes
Faecal Coliforms | 150 | <1 | yes
Ammonia | 2 | 0.1 | yes
Total Nitrogen | 10 | 3.14 | yes
PH | 6.5-8.5 | 7.8 | yes
Phophorus | 0.5 | 0.448 | yes
TSS | 10 | 1 | yes
EPA identification Number 3, Reporting period July-October 2016
* Refer to License No 20188 Average and percentile limits are only applied annualy for routine monitoring data